## GAUGE_NEW
id | domain_id | number | title | main_group | sub_group | visual_type | visual_link | visual_description | next_step | show_map | last_step | map_from_previous_link | enable_skip | skip_to_step | map_from_beginning_link | value_type | value_hint | unit | default_value | default_from_value | default_to_value | report_description
1 | 1 |  | WELCOME | GENERAL CHECKUP | SAFETY ITEMS | IMAGE | 1_generator_room | Welcome to the generator room. You are going to inspect the generator room now. | 2 | 0 | 0 |  | 0 |  |  | NONE
2 | 1 |  | SAFETY - EAR PROTECTION | GENERAL CHECKUP | SAFETY ITEMS | IMAGE | 2_ear_protection | Please wear ear protection device before you go inside the generator room. | 3 | 1 | 0 | 2_safety_ear_protection | 0 |  |  | NONE
3 | 1 |  | SAFETY - HELMET WITH LIGHT | GENERAL CHECKUP | SAFETY ITEMS | IMAGE | 3_helmet_with_light | Please wear a safety helmet with light before enter the generator room. | 4 | 0 | 0 |  | 0 |  |  | NONE
4 | 1 |  | SAFETY - SWITCH ON LIGHT | GENERAL CHECKUP | SAFETY ITEMS | IMAGE | 4_switch_on_light | Please switch on helmet light. | 5 | 0 | 0 |  | 0 |  |  | NONE
5 | 1 |  | SYNCHRONIZE PANEL | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 5_synchronizing_panel | Now you are about to inspect the synchronize panel. Be sure you are currently placed in front of the synchronize panel. | 6 | 1 | 0 | 5_synchronizing_panel | 1 | 21 |  | NONE
6 | 1 |  | SYNC. PANEL - EMERGENCY SWITCH | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 6_emergency_switch | Check whether emergency switch of synchronize panel is working. | 7 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Emergency Switch
7 | 1 |  | SYNC. PANEL - SYS. CONTROL SWITCH | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 7_system_control_switch | Check system control switch | 8 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | System Control Switch
8 | 1 |  | SYNC. PANEL - LOAD DEMAND SWITCH | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 8_load_demand_switch | Check load demand switch | 9 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Load Demant Switch
9 | 1 |  | SYNC. PANEL - LOAD DEMAND DROPOUT | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 9_load_demand_dropout | Check demand dropout | 10 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  | 80 |  |  | Load Demand Dropout
10 | 1 |  | SYNC. PANEL - LOAD DEMAND PICKUP | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 10_load_demand_pickup | Check demand pickup | 11 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  | 75 |  |  | Load Demand Pickup
11 | 1 |  | SYNC. PANEL - LOAD UNIT SELECTION | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 11_load_unit_selection | Check load unit selection | 12 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  | 9 |  |  | Load Unit Selection
12 | 1 |  | SYNC. PANEL - EARTH FAULT RELAY 01 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 12_earth_fault_relay_1 | Check Earth Fault Relay 1 | 13 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Earth Fault Relay 1
13 | 1 |  | SYNC. PANEL - EARTH FAULT RELAY 02 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 13_earth_fault_relay_2 | Check Earth Fault Relay 2 | 14 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Earth Fault Relay 2
14 | 1 |  | SYNC. PANEL - EARTH FAULT RELAY 03 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 14_earth_fault_relay_3 | Check Earth Fault Relay 3 | 15 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Earth Fault Relay 3
15 | 1 |  | SYNC. PANEL - POWER COMMAND PANEL | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 15_power_command_panel | Check Power Command Panel | 16 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Power Command Panel
16 | 1 |  | SYNC. PANEL - ANALYSER READING | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 16_analyser_reading | Check Analyzer Reading | 17 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Analyzer Reading
17 | 1 |  | SYNC. PANEL - INDICATOR LIGHT 01 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 17_indicator_light_1 | Check Indicator Lights (RED/YELLOW/BLUE) Lighting and report whethe lights are OK or NOT OK. | 18 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Indicator Light 01
18 | 1 |  | SYNC. PANEL - INDICATOR LIGHT 02 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 18_indicator_light_2 | Check Indicator Lights (RED/YELLOW/BLUE) Lighting and report whethe lights are OK or NOT OK. | 19 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Indicator Light 02
19 | 1 |  | SYNC. PANEL - INDICATOR LIGHT 03 | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 19_indicator_light_3 | Check Indicator Lights (RED/YELLOW/BLUE) Lighting and report whethe lights are OK or NOT OK. | 20 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Indicator Light 03
20 | 1 |  | SYNC. PANEL - MOTORISED BREAKER | GENERAL CHECKUP | SYNCHRONIZE PANEL | IMAGE | 18_motorised_breaker_position | Check Motorized Breaker Position | 21 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Motorized Breaker Position
21 | 1 |  | GENERATOR 01 - OFF MODE | GENERATOR 01 | OFF MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 01 in off mode. Be sure you are currently placed in front of the Generator 01. | 22 | 1 | 0 | 19_generator_01_off_mode | 1 | 31 |  | NONE
22 | 1 |  | GEN. 01 - PANEL BOARD | GENERATOR 01 | OFF MODE | IMAGE | 20_generator_01_panel_board | Check generator 01 control panel switch and report whether control panel switch is OK or NOT OK. | 23 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Control panel switch off
23 | 1 |  | GEN. 01 - BATTERY PACK | GENERATOR 01 | OFF MODE | IMAGE | 21_generator_01_battery_pack | Check generator 01 battery water level and report whether water level is OK or NOT OK. | 24 | 1 | 0 | 21_generator_01_battery_pack | 0 |  |  | BOOLEAN | [5 empty] | Battery water level
24 | 1 |  | GEN. 01 - ENGINE OIL LEAKS | GENERATOR 01 | OFF MODE | IMAGE | 22_generator_01_oil_leaks | Check generator 01 body for oil leaks and report OK if oil leaks not available and NOT OK if oil leaks available. | 25 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Engine oil leaks (visual inspection)
25 | 1 |  | GEN. 01 - ALTERNATOR BELT TENSION | GENERATOR 01 | OFF MODE | IMAGE | 23_generator_01_alternator | Check generator 01 alternator for it's belt tension and report whether belt tension is OK or NOT OK. | 26 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Alternator belt tension/condition
26 | 1 |  | GEN. 01 - ENGINE OIL LEVEL | GENERATOR 01 | OFF MODE | VIDEO | 24_generator_01_engine_oil_level | Check Generator 01 engine oil level and report oil level is OK or NOT OK. | 27 | 1 | 0 | 24_generator_01_engine_oil_level | 0 |  |  | BOOLEAN | [5 empty] | Engine oil level
27 | 1 |  | GEN. 01 - AIR FILTER INDICATOR | GENERATOR 01 | OFF MODE | IMAGE | 25_generator_01_air_filter | Check Generator 01 air filter and report air filter is OK or NOT OK. | 28 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Air filter condition
28 | 1 |  | GEN. 01 - RADIATOR FAN TENSION | GENERATOR 01 | OFF MODE | VIDEO | 26_generator_01_radiator_fan_tension | Check Generator 01 radiator for fan tension and report whether fan tension is OK or NOT OK. | 29 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator fan tension/condition
29 | 1 |  | GEN. 01 - RADIATOR COOLEANT | GENERATOR 01 | OFF MODE | VIDEO | 28_generator_01_radiator_coolent_level | Check Generator 01 radiator coolant level and report whether coolant level is OK or NOT OK. | 30 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator cooleant level
30 | 1 |  | GEN. 01 - BATTERY VOLTAGE | GENERATOR 01 | OFF MODE | VIDEO | 29_generator_01_battery_voltage | Check Generator 01 battery voltage and report battery voltage value. | 31 | 1 | 0 | 29_generator_01_battery_voltage | 0 |  |  | DECIMAL |  | V |  | 24 | 27 | Battery voltage
31 | 1 |  | GENERATOR 02 - OFF MODE | GENERATOR 02 | OFF MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 02 in off mode. Be sure you are currently placed in front of the Generator 02. | 32 | 1 | 0 | 30_generator_02_off_mode | 1 | 41 |  | NONE
32 | 1 |  | GEN. 02 - PANEL BOARD | GENERATOR 02 | OFF MODE | IMAGE | 20_generator_01_panel_board | Check generator 02 control panel switch and report whether control panel switch is OK or NOT OK. | 33 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Control panel switch off
33 | 1 |  | GEN. 02 - BATTERY PACK | GENERATOR 02 | OFF MODE | IMAGE | 21_generator_01_battery_pack | Check generator 02 battery water level and report whether water level is OK or NOT OK. | 34 | 1 | 0 | 32_generator_02_battery_pack | 0 |  |  | BOOLEAN | [5 empty] | Battery water level
34 | 1 |  | GEN. 02 - ENGINE OIL LEAKS | GENERATOR 02 | OFF MODE | IMAGE | 22_generator_01_oil_leaks | Check generator 02 body for oil leaks and report OK if oil leaks not available and NOT OK if oil leaks available. | 35 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Engine oil leaks (visual inspection)
35 | 1 |  | GEN. 02 - ALTERNATOR BELT TENSION | GENERATOR 02 | OFF MODE | IMAGE | 23_generator_01_alternator | Check generator 02 alternator for it's belt tension and report whether belt tension is OK or NOT OK. | 36 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Alternator belt tension/condition
36 | 1 |  | GEN. 02 - ENGINE OIL LEVEL | GENERATOR 02 | OFF MODE | VIDEO | 24_generator_01_engine_oil_level | Check Generator 02 engine oil level and report oil level is OK or NOT OK. | 37 | 1 | 0 | 35_generator_02_engine_oil_level | 0 |  |  | BOOLEAN | [5 empty] | Engine oil level
37 | 1 |  | GEN. 02 - AIR FILTER INDICATOR | GENERATOR 02 | OFF MODE | IMAGE | 25_generator_01_air_filter | Check Generator 02 air filter and report air filter is OK or NOT OK. | 38 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Air filter condition
38 | 1 |  | GEN. 02 - RADIATOR FAN TENSION | GENERATOR 02 | OFF MODE | VIDEO | 26_generator_01_radiator_fan_tension | Check Generator 02 radiator for fan tension and report whether fan tension is OK or NOT OK. | 39 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator fan tension/condition
39 | 1 |  | GEN. 02 - RADIATOR COOLEANT | GENERATOR 02 | OFF MODE | VIDEO | 28_generator_01_radiator_coolent_level | Check Generator 02 radiator coolant level and report whether coolant level is OK or NOT OK. | 40 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator cooleant level
40 | 1 |  | GEN. 02 - BATTERY VOLTAGE | GENERATOR 02 | OFF MODE | VIDEO | 29_generator_01_battery_voltage | Check Generator 02 battery voltage and report battery voltage value. | 41 | 1 | 0 | 40_generator_02_battery_voltage | 0 |  |  | DECIMAL |  | V |  | 24 | 27 | Battery voltage
41 | 1 |  | GENERATOR 03 - OFF MODE | GENERATOR 03 | OFF MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 03 in off mode. Be sure you are currently placed in front of the Generator 03. | 42 | 1 | 0 | 41_generator_03_off_mode | 1 | 51 |  | NONE
42 | 1 |  | GEN. 03 - PANEL BOARD | GENERATOR 03 | OFF MODE | IMAGE | 20_generator_01_panel_board | Check generator 03 control panel switch and report whether control panel switch is OK or NOT OK. | 43 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Control panel switch off
43 | 1 |  | GEN. 03 - BATTERY PACK | GENERATOR 03 | OFF MODE | IMAGE | 21_generator_01_battery_pack | Check generator 03 battery water level and report whether water level is OK or NOT OK. | 44 | 1 | 0 | 43_generator_03_battery_pack | 0 |  |  | BOOLEAN | [5 empty] | Battery water level
44 | 1 |  | GEN. 03 - ENGINE OIL LEAKS | GENERATOR 03 | OFF MODE | IMAGE | 22_generator_01_oil_leaks | Check generator 03 body for oil leaks and report OK if oil leaks not available and NOT OK if oil leaks available. | 45 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Engine oil leaks (visual inspection)
45 | 1 |  | GEN. 03 - ALTERNATOR BELT TENSION | GENERATOR 03 | OFF MODE | IMAGE | 23_generator_01_alternator | Check generator 03 alternator for it's belt tension and report whether belt tension is OK or NOT OK. | 46 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Alternator belt tension/condition
46 | 1 |  | GEN. 03 - ENGINE OIL LEVEL | GENERATOR 03 | OFF MODE | VIDEO | 24_generator_01_engine_oil_level | Check Generator 03 engine oil level and report oil level is OK or NOT OK. | 47 | 1 | 0 | 46_generator_03_engine_oil_level | 0 |  |  | BOOLEAN | [5 empty] | Engine oil level
47 | 1 |  | GEN. 03 - AIR FILTER INDICATOR | GENERATOR 03 | OFF MODE | IMAGE | 25_generator_01_air_filter | Check Generator 03 air filter and report air filter is OK or NOT OK. | 48 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Air filter condition
48 | 1 |  | GEN. 03 - RADIATOR FAN TENSION | GENERATOR 03 | OFF MODE | VIDEO | 26_generator_01_radiator_fan_tension | Check Generator 03 radiator for fan tension and report whether fan tension is OK or NOT OK. | 49 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator fan tension/condition
49 | 1 |  | GEN. 03 - RADIATOR COOLEANT | GENERATOR 03 | OFF MODE | IMAGE | 50_generator_03_radiator_cooleant | Check Generator 03 radiator coolant level and report whether coolant level is OK or NOT OK. | 50 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator cooleant level
50 | 1 |  | GEN. 03 - BATTERY VOLTAGE | GENERATOR 03 | OFF MODE | VIDEO | 29_generator_01_battery_voltage | Check Generator 03 battery voltage and report battery voltage value. | 51 | 1 | 0 | 51_generator_03_battery_voltage | 0 |  |  | DECIMAL |  | V |  | 24 | 27 | Battery voltage
51 | 1 |  | DEISAL TANK | GENERAL CHECKUP | SITE INSPECTION | IMAGE | 52_deisal_tank | Check Diesel tank | 52 | 1 | 0 | 52_deisal_tank | 1 | 52 |  | DECIMAL |  | l |  | 3000 | 20000 | Diesel tank
52 | 1 |  | GENERATOR 03 - RUN MODE | GENERATOR 03 | RUN MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 03 in run mode. Be sure you are currently placed in front of the Generator 03. | 53 | 1 | 0 | 53_generator_03_run_mode | 1 | 63 |  | NONE
53 | 1 |  | GEN. 03 - ERROR MESSAGES | GENERATOR 03 | RUN MODE | IMAGE | 54_generator_03_error_messages | Check generator 03 for error messages. | 54 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Error message
54 | 1 |  | GEN. 03 - OIL PRESSURE | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 for oil pressure. | 55 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Pa |  | 20 | 80 | Oil pressure
55 | 1 |  | GEN. 03 - OIL TEMPERATURE | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 for oil temperature. | 56 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 160 | 210 | Oil Temperature
56 | 1 |  | GEN. 03 - COOLEANT TEMPERATURE | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 for coolant temperature. | 57 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 170 | 210 | Coolant Temperature
57 | 1 |  | GEN. 03 - FREQUENCY | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 frequency. | 58 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Hz |  | 49.5 | 50.5 | Frequency
58 | 1 |  | GEN. 03 - CURRENT | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 current. | 59 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  |  |  | Current
59 | 1 |  | GEN. 03 - LINE VOLTAGE | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 line voltage. | 60 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 380 | 415 | Line voltage
60 | 1 |  | GEN. 03 - PHASE VOLTAGE | GENERATOR 03 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 03 phase voltage. | 61 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 220 | 240 | Phase voltage
61 | 1 |  | GEN. 03 - NOICE INSPECTION | GENERATOR 03 | RUN MODE | NONE |  | Inspect generator 03 for noises. | 62 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Noice inspection
62 | 1 |  | GEN. 03 - GENERAL INSPECTION | GENERATOR 03 | RUN MODE | NONE |  | Inspect generator 03 for general abnormalities like steam or smoke. | 63 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | General inspection
63 | 1 |  | GENERATOR 02 - RUN MODE | GENERATOR 02 | RUN MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 02 in run mode. Be sure you are currently placed in front of the Generator 02. | 64 | 1 | 0 | 64_generator_02_run_mode | 1 | 74 |  | NONE
64 | 1 |  | GEN. 02 - ERROR MESSAGES | GENERATOR 02 | RUN MODE | IMAGE | 54_generator_03_error_messages | Check generator 02 for error messages. | 65 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Error message
65 | 1 |  | GEN. 02 - OIL PRESSURE | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 for oil pressure. | 66 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Pa |  | 20 | 80 | Oil pressure
66 | 1 |  | GEN. 02 - OIL TEMPERATURE | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 for oil temperature. | 67 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 160 | 210 | Oil Temperature
67 | 1 |  | GEN. 02 - COOLEANT TEMPERATURE | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 for coolant temperature. | 68 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 170 | 210 | Coolant Temperature
68 | 1 |  | GEN. 02 - FREQUENCY | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 frequency. | 69 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Hz |  | 49.5 | 50.5 | Frequency
69 | 1 |  | GEN. 02 - CURRENT | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 current. | 70 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 2700 | Current
70 | 1 |  | GEN. 02 - LINE VOLTAGE | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 line voltage. | 71 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 380 | 415 | Line voltage
71 | 1 |  | GEN. 02 - PHASE VOLTAGE | GENERATOR 02 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 02 phase voltage. | 72 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 220 | 240 | Phase voltage
72 | 1 |  | GEN. 02 - NOICE INSPECTION | GENERATOR 02 | RUN MODE | NONE |  | Inspect generator 02 for noises. | 73 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Noice inspection
73 | 1 |  | GEN. 02 - GENERAL INSPECTION | GENERATOR 02 | RUN MODE | NONE |  | Inspect generator 02 for general abnormalities like steam or smoke. | 74 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | General inspection
74 | 1 |  | GENERATOR 01 - RUN MODE | GENERATOR 01 | RUN MODE | IMAGE | 19_generator_01_off_mode | Now you are about to inspect the Generator 01 in run mode. Be sure you are currently placed in front of the Generator 01. | 75 | 1 | 0 | 75_generator_01_run_mode | 1 | 85 |  | NONE
75 | 1 |  | GEN. 01 - ERROR MESSAGES | GENERATOR 01 | RUN MODE | IMAGE | 54_generator_03_error_messages | Check generator 01 for error messages. | 76 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Error message
76 | 1 |  | GEN. 01 - OIL PRESSURE | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 for oil pressure. | 77 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Pa |  | 20 | 80 | Oil pressure
77 | 1 |  | GEN. 01 - OIL TEMPERATURE | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 for oil temperature. | 78 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 160 | 210 | Oil Temperature
78 | 1 |  | GEN. 01 - COOLEANT TEMPERATURE | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 for coolant temperature. | 79 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 170 | 210 | Coolant Temperature
79 | 1 |  | GEN. 01 - FREQUENCY | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 frequency. | 80 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Hz |  | 49.5 | 50.5 | Frequency
80 | 1 |  | GEN. 01 - CURRENT | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 current. | 81 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 2700 | Current
81 | 1 |  | GEN. 01 - LINE VOLTAGE | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 line voltage. | 82 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 380 | 415 | Line voltage
82 | 1 |  | GEN. 01 - PHASE VOLTAGE | GENERATOR 01 | RUN MODE | VIDEO | 55_oil_pressure | Check generator 01 phase voltage. | 83 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 220 | 240 | Phase voltage
83 | 1 |  | GEN. 01 - NOICE INSPECTION | GENERATOR 01 | RUN MODE | NONE |  | Inspect generator 01 for noises. | 84 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Noice inspection
84 | 1 |  | GEN. 01 - GENERAL INSPECTION | GENERATOR 01 | RUN MODE | NONE |  | Inspect generator 01 for general abnormalities like steam or smoke. | 85 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | General inspection
85 | 1 |  | SITE - ATANUATER | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Check attenuator front and surround | 86 | 1 | 0 | 86_site_inspection_atanuater | 1 | 89 |  | BOOLEAN | [5 empty] | Attenuator
86 | 1 |  | SITE - SEILING | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Check ceiling appearance and lights | 87 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Ceiling
87 | 1 |  | SITE - FLOOR | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Check floor general appearance | 88 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Floor
88 | 1 |  | SITE - OIL LINES | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Check oil lines general appearance | 89 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil lines
89 | 1 |  | FINISH | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Well done. You have finished checking generator room. |  | 0 | 1 |  | 0 |  |  | NONE | [5 empty] | Finish
101 | 2 |  | WELCOME | ENTRANCE | ENTRANCE | IMAGE | 100_chiller_room | Welcome to the chiller room. You are going to inspect the chiller room now. | 102 | 0 | 0 |  | 0 |  |  | NONE | [5 empty] | Welcome
102 | 2 |  | CHIL. A - CHILLER CONTROL PANEL | CHILLER - A | CHILLER CONTROL PANEL | IMAGE | 101_chiller_control_panel | Now you are going to inspect Chiller A. Be sure you are currently placed in front of the Chiller A. | 103 | 1 | 0 | chiller_a | 1 | 108 |  | NONE
103 | 2 |  | CHIL. A - COOLING TOWER 01 | CHILLER - A | CHILLER CONTROL PANEL | NONE |  | Check cooling tower 01 run mode. | 104 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check cooling tower 01 run mode.
104 | 2 |  | CHIL. A - COOLING TOWER 02 | CHILLER - A | CHILLER CONTROL PANEL | NONE |  | Check cooling tower 02 run mode. | 105 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check cooling tower 02 run mode.
105 | 2 |  | CHIL. A - CONDENSER PUMP | CHILLER - A | CHILLER CONTROL PANEL | NONE |  | Check condenser pump 1 or 2 run. | 106 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check condenser pump 1 or 2 run.
106 | 2 |  | CHIL. A - WATER PUMP | CHILLER - A | CHILLER CONTROL PANEL | NONE |  | Check chiller water pump V.S.D 1 run | 107 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check chiller water pump V.S.D 1 run
107 | 2 |  | CHIL. A - WATER PUMP | CHILLER - A | CHILLER CONTROL PANEL | NONE |  | Check chiller water pump V.S.D 2 run | 108 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check chiller water pump V.S.D 2 run
108 | 2 |  | CHIL. A - WATER PRESSURE | CHILLER - A | CHILLER WATER PRESSURE | IMAGE | 20161115_121039 | Now you are going to inspect Chiller - A water pressure | 109 | 0 | 0 |  | 1 | 113 |  | NONE
109 | 2 |  | CHIL. A - CHILLED WATER PRESSURE | CHILLER - A | CHILLER WATER PRESSURE | NONE |  | Chilled water IN pressure | 110 | 0 | 0 |  | 0 |  |  | DECIMAL |  | psi |  | 35 | 45 | Chilled water in pressure
110 | 2 |  | CHIL. A - CHILLED WATER PRESSURE | CHILLER - A | CHILLER WATER PRESSURE | NONE |  | Chilled water OUT pressure | 111 | 0 | 0 |  | 0 |  |  | DECIMAL |  | psi |  | 30 | 40 | Chilled water out pressure
111 | 2 |  | CHIL. A - CONDENSER PRESSURE | CHILLER - A | CHILLER WATER PRESSURE | NONE |  | Condenser water IN pressure | 112 | 0 | 0 |  | 0 |  |  | DECIMAL |  | psi | 21 |  |  | Condenser water in pressure
112 | 2 |  | CHIL. A - CONDENSER PRESSURE | CHILLER - A | CHILLER WATER PRESSURE | NONE |  | Condenser water OUT pressure | 113 | 0 | 0 |  | 0 |  |  | DECIMAL |  | psi | 11 |  |  | Condenser water out pressure
113 | 2 |  | CHIL. A - OIL LEVEL | CHILLER - A | OIL LEVEL | IMAGE | 113_oil_level | Oil level | 114 | 0 | 0 |  | 1 | 114 |  | BOOLEAN | [5 empty] | Oil level
114 | 2 |  | CHIL. A - CONTROL DISPLAY | CHILLER - A | CHILLER CONTROL DISPLAY | IMAGE | 108_chiller_control_display | Now you are going to inspect Chiller - A control display. | 115 | 0 | 0 |  | 1 | 136 |  | NONE
115 | 2 |  | CHIL. A - REFRIGERANT PRESSURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Refrigerant Pressure | 116 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kPa |  | 250 | 300 | Refrigerant Pressure
116 | 2 |  | CHIL. A - REFRIGERANT TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Refrigerant temperature | 117 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 6 | 12 | Refrigerant temperature
117 | 2 |  | CHIL. A - CHILL WATER IN TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Chilled water IN temperature | 118 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 8 | 20 | chill water in temperature
118 | 2 |  | CHIL. A - CHILL WATER OUT TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Chilled water OUT temperature | 119 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 6 | 25 | chill water out temperature
119 | 2 |  | CHIL. A - REFRIGERANT PRESSURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Condenser Refrigerant pressure | 120 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kPa |  | 600 | 1000 | Condenser Refrigerant pressure
120 | 2 |  | CHIL. A - REFRIGERANT TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Condenser Refrigerant temperature | 121 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 28 | 38 | Condenser Refrigerant temperature
121 | 2 |  | CHIL. A - CONDENSER WATER IN TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Condenser water IN temperature | 122 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 20 | 32 | Condenser water in temperature
122 | 2 |  | CHIL. A - CONDENSER WATER OUT TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Condenser water OUT temperature | 123 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 0 | 35 | Condenser water out temperature
123 | 2 |  | CHIL. A - RECLAIM DELTA T | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Reclaim delta T | 124 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 5 | 25 | Reclaim delta T
124 | 2 |  | CHIL. A - OIL RECLAIM OUTPUT | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Oil reclaim output | 125 | 0 | 0 |  | 0 |  |  | DECIMAL |  | % |  | 0 | 60 | Oil reclaim output
125 | 2 |  | CHIL. A - OIL PRESSURE DELTA P | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Oil pressure delta p | 126 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kPa |  | 150 | 220 | Oil pressure delta P
126 | 2 |  | CHIL. A - OIL SUMP TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Oil sump temperature | 127 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 30 | 40 | Oil sump temperature
127 | 2 |  | CHIL. A - AVERAGE LINE CURRENT | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Average line current | 128 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 400 | Average line current
128 | 2 |  | CHIL. A - AVERAGE LINE VOLTAGE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Average line voltage | 129 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 385 | 415 | Average line voltage
129 | 2 |  | CHIL. A - LINE KW | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Line kW | 130 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kW |  | 0 | 300 | Line kW
130 | 2 |  | CHIL. A - AVERAGE LOAD CURRENT | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Average load current | 131 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 400 | Average load current
131 | 2 |  | CHIL. A - INVERTER TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Inverter temperature | 132 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 35 | 45 | Inverter temperature
132 | 2 |  | CHIL. A - RECTIFIER TEMPERATURE | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Rectifier temperature | 133 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 35 | 45 | Rectifier temperature
133 | 2 |  | CHIL. A - VFD COOLENT FLOW | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | VFD coolant flow | 134 | 0 | 0 |  | 0 |  |  | DECIMAL |  | % | 100 |  |  | VFD coolant flow
134 | 2 |  | CHIL. A - TOTAL CURRENT | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Total current | 135 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 500 | Total current
135 | 2 |  | CHIL. A - MOTOR LOAD | CHILLER - A | CHILLER CONTROL DISPLAY | NONE |  | Motor load | 136 | 0 | 0 |  | 0 |  |  | DECIMAL |  | % |  | 0 | 100 | Motor load
136 | 2 |  | CHIL. B - CHILLER CONTROL PANEL | CHILLER - B | CHILLER CONTROL PANEL | IMAGE | 20161115_121238 | Now you are going to inspect Chiller B. Be sure you are currently placed in front of the Chiller B. | 137 | 1 | 0 | chiller_b | 1 | 142 |  | NONE
137 | 2 |  | CHIL. B - COOLING TOWER 01 | CHILLER - B | CHILLER CONTROL PANEL | NONE |  | Check cooling tower VSD 01 run mode. | 138 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check cooling tower 01 run mode.
138 | 2 |  | CHIL. B - COOLING TOWER 02 | CHILLER - B | CHILLER CONTROL PANEL | NONE |  | Check cooling tower VSD 02 run mode. | 139 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check cooling tower 02 run mode.
139 | 2 |  | CHIL. B - CONDENSER PUMP | CHILLER - B | CHILLER CONTROL PANEL | NONE |  | Check condenser pump 1 run. | 140 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check condenser pump 1 or 2 run.
140 | 2 |  | CHIL. B - WATER PUMP | CHILLER - B | CHILLER CONTROL PANEL | NONE |  | Check chiller water pump V.S.D 1 run | 141 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check chiller water pump V.S.D 1 run
141 | 2 |  | CHIL. B - WATER PUMP | CHILLER - B | CHILLER CONTROL PANEL | NONE |  | Check chiller water pump V.S.D 2 run | 142 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check chiller water pump V.S.D 2 run
142 | 2 |  | CHIL. B - WATER PRESSURE | CHILLER - B | CHILLER WATER PRESSURE | IMAGE | 20161115_121334 | Now you are going to inspect Chiller - B water pressure. | 143 | 0 | 0 |  | 1 | 147 |  | NONE
143 | 2 |  | CHIL. B - CHILLED WATER PRESSURE | CHILLER - B | CHILLER WATER PRESSURE | NONE |  | Chiller water entering pressure | 144 | 0 | 0 |  | 0 |  |  | DECIMAL |  | PSI |  | 35 | 45 | Chilled water in pressure
144 | 2 |  | CHIL. B - CHILLED WATER PRESSURE | CHILLER - B | CHILLER WATER PRESSURE | NONE |  | Chilled water out pressure | 145 | 0 | 0 |  | 0 |  |  | DECIMAL |  | PSI |  | 30 | 40 | Chilled water out pressure
145 | 2 |  | CHIL. B - CONDENSER PRESSURE | CHILLER - B | CHILLER WATER PRESSURE | NONE |  | Condenser water in pressure | 146 | 0 | 0 |  | 0 |  |  | DECIMAL |  | PSI | 21 |  |  | Condenser water in pressure
146 | 2 |  | CHIL. B - CONDENSER PRESSURE | CHILLER - B | CHILLER WATER PRESSURE | NONE |  | Condenser water out pressure | 147 | 0 | 0 |  | 0 |  |  | DECIMAL |  | PSI | 11 |  |  | Condenser water out pressure
147 | 2 |  | CHIL. B - CONTROL DISPLAY | CHILLER - B | CHILLER CONTROL DISPLAY | IMAGE | 20161115_121431 | Now you are going to inspect Chiller - B control display. | 148 | 1 | 0 | chiller_c | 1 | 164 |  | NONE
148 | 2 |  | CHIL. B - CHILLER TOTAL LOAD | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Chiller total load % | 149 | 0 | 0 |  | 0 |  |  | DECIMAL |  | % |  | 0 | 100 | Chiller total load %
149 | 2 |  | CHIL. B - TOTAL OPERATING CURRENT | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Chiller total operating current | 150 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 450 | Chiller total operating current
150 | 2 |  | CHIL. B - CHILLER SET POINT | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Chiller set point | 151 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 8 | 25 | Chiller set point
151 | 2 |  | CHIL. B - WATER ENTERING TEMP. | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Chiller water entering temperature - EWT | 152 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 6 | 25 | Chiller water entering temperature EWT
152 | 2 |  | CHIL. B - WATER LEVING TEMP. | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Chiller water leaving temperature - LWT | 153 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  |  |  | Chiller water leving temperature LWT
153 | 2 |  | CHIL. B - WATER ENTERING TEMP. | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Condenser water entering temperature | 154 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 20 | 32 | Condenser water entering temperature
154 | 2 |  | CHIL. B/CIRCUIT A - WATER LEVING TEMP. | CHILLER - B | CHILLER CONTROL DISPLAY | NONE |  | Condenser water leaving temperature | 155 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 0 | 35 | Condenser water leving temperature
155 | 2 |  | CHIL. B/CIRCUIT A - CIRCUIT A LOAD | CHILLER - B | CIRCUIT A | NONE |  | Circuit load % 0- cap | 156 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  |  | 0 | 100 | Curcuit load % 0- cap
156 | 2 |  | CHIL. B/CIRCUIT A - DISCHARGE PRESSURE | CHILLER - B | CIRCUIT A | NONE |  | Discharge pressure -DP | 157 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 0 | 1000 | Discharge pressure -DP
157 | 2 |  | CHIL. B/CIRCUIT A - SUCTION PRESSURE | CHILLER - B | CIRCUIT A | NONE |  | Suction pressure | 158 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 250 | 300 | Suction pressure
158 | 2 |  | CHIL. B/CIRCUIT A - OPERATING CURRENT | CHILLER - B | CIRCUIT A | NONE |  | Compressure/Motor operating current | 159 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 200 | Compresure / Motor operating current
159 | 2 |  | CHIL. B/CIRCUIT A - SATURATERD TEMPERATURE | CHILLER - B | CIRCUIT A | NONE |  | Saturaterd condenser temperature - SCT | 160 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 28 | 38 | Saturated condenser temperature - SCT
160 | 2 |  | CHIL. B/CIRCUIT A - SATURATERD TEMPERATURE | CHILLER - B | CIRCUIT A | NONE |  | Saturaterd suction temprature - SST | 161 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 6 | 10 | Saturated suction temperature - SST
161 | 2 |  | CHIL. B/CIRCUIT A - EXV POSITION | CHILLER - B | CIRCUIT A | NONE |  | EXV Position % - EXV | 162 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  |  | 0 | 100 | EXV Position % - EXV
162 | 2 |  | CHIL. B/CIRCUIT A - OIL PRESSURE | CHILLER - B | CIRCUIT A | NONE |  | Oil pressure (kpa) - OP | 163 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 600 | 1000 | Oil presure (kpa) - OP
163 | 2 |  | CHIL. B/CIRCUIT A - DISCHARGE GAS TEMPERATURE | CHILLER - B | CIRCUIT A | NONE |  | Discharge gas temperature - DGT | 164 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 30 | 50 | Discharge gas temperature - DGT
164 | 2 |  | CHIL. B/CIRCUIT B - CIRCUIT B LOAD | CHILLER - B | CIRCUIT B | NONE |  | Circuit load % 0- cap | 165 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  |  | 0 | 100 | Curcuit load % 0- cap
165 | 2 |  | CHIL. B/CIRCUIT B - DISCHARGE PRESSURE | CHILLER - B | CIRCUIT B | NONE |  | Discharge pressure -DP | 166 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 0 | 1000 | Discharge pressure -DP
166 | 2 |  | CHIL. B/CIRCUIT B - SUCTION PRESSURE | CHILLER - B | CIRCUIT B | NONE |  | Suction pressure | 167 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 250 | 300 | Suction pressure
167 | 2 |  | CHIL. B/CIRCUIT B - OPERATING CURRENT | CHILLER - B | CIRCUIT B | NONE |  | Compressure/Motor operating current | 168 | 0 | 0 |  | 0 |  |  | DECIMAL |  | A |  | 0 | 200 | Compresure / Motor operating current
168 | 2 |  | CHIL. B/CIRCUIT B - SATURATERD TEMPERATURE | CHILLER - B | CIRCUIT B | NONE |  | Saturaterd condenser temperature - SCT | 169 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 28 | 38 | Saturated condenser temperature - SCT
169 | 2 |  | CHIL. B/CIRCUIT B - SATURATERD TEMPERATURE | CHILLER - B | CIRCUIT B | NONE |  | Saturaterd suction temprature - SST | 170 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 6 | 10 | Saturated suction temperature - SST
170 | 2 |  | CHIL. B/CIRCUIT B - EXV POSITION | CHILLER - B | CIRCUIT B | NONE |  | EXV Position % - EXV | 171 | 0 | 0 |  | 0 |  |  | DECIMAL |  |  |  | 0 | 100 | EXV Position % - EXV
171 | 2 |  | CHIL. B/CIRCUIT B - OIL PRESSURE | CHILLER - B | CIRCUIT B | NONE |  | Oil pressure (kpa) - OP | 172 | 0 | 0 |  | 0 |  |  | DECIMAL |  | KPA |  | 600 | 1000 | Oil presure (kpa) - OP
172 | 2 |  | CHIL. B/CIRCUIT B - DISCHARGE GAS TEMPERATURE | CHILLER - B | CIRCUIT B | NONE |  | Discharge gas temperature - DGT | 173 | 0 | 0 |  | 0 |  |  | DECIMAL |  | C |  | 30 | 50 | Discharge gas temperature - DGT
173 | 2 |  | VISUAL INSPECTION | VISUAL INSPECTION | CHILLER WATER PUMPS | IMAGE | 20161115_121645 | Condenser warer pumps 1/2/3/4 notice and visual inspection | 174 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Chiller water pumps
174 | 2 |  | VISUAL INSPECTION | VISUAL INSPECTION | CONDENSER WATER PUMPS | IMAGE | 20161115_121753 | Chiller warer pumps 1/2/3/4 notice and visual inspection | 175 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Condenser water pumps
175 | 2 |  | FINISH | GENERAL CHECKUP | SITE INSPECTION | NONE |  | Well done. You have finished checking chiller room. |  | 0 | 1 |  | 0 |  |  | NONE | [5 empty] | Finish
200 | 3 |  | WELCOME | GENERAL CHECKUP | WELCOME | NONE |  | Welcome to the compressor room. You are going to inspect the compressor room now. | 201 | 0 | 0 |  | 0 |  |  | NONE | [5 empty] | Welcome
201 | 3 |  | ENTRANCE OF COMPRESSOR ROOM | GENERAL CHECKUP | ENTRANCE OF COMPRESSOR ROOM | IMAGE | imag0016 | Entrance of Compressor room | 202 | 0 | 0 |  | 0 |  |  | NONE | [5 empty] | Entrance of Compressor room
202 | 3 |  | SELECT SAFTY ITEM | GENERAL CHECKUP | SELECT SAFTY ITEM | IMAGE | imag0017 | Select safety item | 203 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Select safety item
203 | 3 |  | COMPRESSOR 05 | COMPRESSOR 05 | STANDBY MODE | IMAGE | compressor_05 | You are about to inspect compressor 05 | 204 | 1 | 0 | com-01 | 1 | 212 |  | NONE | [5 empty] | compressor 05
204 | 3 |  | OIL LEVEL | COMPRESSOR 05 | STANDBY MODE | IMAGE | img_3887 | Oil level | 205 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil level
205 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 05 | STANDBY MODE | IMAGE | img_3888 | Check oil leaking | 206 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
206 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 05 | STANDBY MODE | IMAGE | img_3890 | Check oil leaking | 207 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
207 | 3 |  | VALVE OPEN | COMPRESSOR 05 | STANDBY MODE | IMAGE | img_3896 | Valve open | 208 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Valve open
208 | 3 |  | AIR PRESSURE | COMPRESSOR 05 | RUN MODE | VIDEO | video_05 | Air pressure | 209 | 0 | 0 |  | 0 |  |  | DECIMAL |  | BAR |  | 6 | 7.5 | Air pressor
209 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 05 | RUN MODE | VIDEO | video_05 | Check coolant temperature | 210 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 70 | 110 | Check coolant tempracher
210 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 05 | RUN MODE | VIDEO | video_05 | Check discharge temperature | 211 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 80 | 95 | Check discharge tempracher
211 | 3 |  | RUNING HOUR | COMPRESSOR 05 | RUN MODE | VIDEO | video_05 | Runing hour | 212 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Runing hour
212 | 3 |  | COMPRESSOR 02 | COMPRESSOR 05 | STANDBY MODE | IMAGE | compressor_02 | You are about to inspect compressor 02 | 213 | 1 | 0 | com-02 | 1 | 221 |  | NONE | [5 empty] | compressor 02
213 | 3 |  | OIL LEVEL | COMPRESSOR 02 | STANDBY MODE | IMAGE | imag0019 | Oil level | 214 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil level
214 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 02 | STANDBY MODE | IMAGE | imag0021 | Check oil leaking | 215 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
215 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 02 | STANDBY MODE | IMAGE | imag0022 | Check oil leaking | 216 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
216 | 3 |  | VALVE OPEN | COMPRESSOR 02 | STANDBY MODE | IMAGE | imag0025 | Valve open | 217 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Valve open
217 | 3 |  | AIR PRESSURE | COMPRESSOR 02 | RUN MODE | VIDEO | video0002 | Air pressure | 218 | 0 | 0 |  | 0 |  |  | DECIMAL |  | BAR |  | 6 | 7.5 | Air pressor
218 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 02 | RUN MODE | VIDEO | video0002 | Check coolant temperature | 219 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 70 | 110 | Check coolant tempracher
219 | 3 |  | CHECK DISCHARGE TEMPERATURE | COMPRESSOR 02 | RUN MODE | VIDEO | video0002 | Check discharge temperature | 220 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 80 | 95 | Check discharge tempracher
220 | 3 |  | RUNING HOUR | COMPRESSOR 02 | RUN MODE | VIDEO | video0002 | Runing hour | 221 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Runing hour
221 | 3 |  | COMPRESSOR 03 | COMPRESSOR 03 | STANDBY MODE | IMAGE | compressor_03 | You are about to inspect compressor 03 | 222 | 1 | 0 | com-03 | 1 | 230 |  | NONE | [5 empty] | compressor 03
222 | 3 |  | OIL LEVEL | COMPRESSOR 03 | STANDBY MODE | IMAGE | imag0026 | Oil level | 223 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil level
223 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 03 | STANDBY MODE | IMAGE | imag0028 | Check oil leaking | 224 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
224 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 03 | STANDBY MODE | IMAGE | imag0032 | Check oil leaking | 225 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
225 | 3 |  | VALVE OPEN | COMPRESSOR 03 | STANDBY MODE | IMAGE | imag0034 | Valve open | 226 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Valve open
226 | 3 |  | AIR PRESSURE | COMPRESSOR 03 | RUN MODE | VIDEO | video0003 | Air pressure | 227 | 0 | 0 |  | 0 |  |  | DECIMAL |  | BAR |  | 6 | 7.5 | Air pressor
227 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 03 | RUN MODE | VIDEO | video0003 | Check coolant temperature | 228 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 70 | 110 | Check coolant tempracher
228 | 3 |  | CHECK DISCHARGE TEMPERATURE | COMPRESSOR 03 | RUN MODE | VIDEO | video0003 | Check discharge temperature | 229 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 80 | 95 | Check discharge tempracher
229 | 3 |  | RUNING HOUR | COMPRESSOR 03 | RUN MODE | VIDEO | video0003 | Runing hour | 230 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Runing hour
230 | 3 |  | COMPRESSOR 04 | COMPRESSOR 04 | STANDBY MODE | IMAGE | compressor_04 | You are about to inspect compressor 04 | 231 | 1 | 0 | com-04 | 1 | 239 |  | NONE | [5 empty] | compressor 04
231 | 3 |  | OIL LEVEL | COMPRESSOR 04 | STANDBY MODE | IMAGE | imag0026 | Oil level | 232 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil level
232 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 04 | STANDBY MODE | IMAGE | imag0028 | Check oil leaking | 233 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
233 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 04 | STANDBY MODE | IMAGE | imag0032 | Check oil leaking | 234 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
234 | 3 |  | VALVE OPEN | COMPRESSOR 04 | STANDBY MODE | IMAGE | imag0034 | Valve open | 235 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Valve open
235 | 3 |  | AIR PRESSURE | COMPRESSOR 04 | RUN MODE | VIDEO | video0003 | Air pressure | 236 | 0 | 0 |  | 0 |  |  | DECIMAL |  | BAR |  | 6 | 7.5 | Air pressor
236 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 04 | RUN MODE | VIDEO | video0003 | Check coolant temperature | 237 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 70 | 110 | Check coolant tempracher
237 | 3 |  | CHECK DISCHARGE TEMPERATURE | COMPRESSOR 04 | RUN MODE | VIDEO | video0003 | Check discharge temperature | 238 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 80 | 95 | Check discharge tempracher
238 | 3 |  | RUNING HOUR | COMPRESSOR 04 | RUN MODE | VIDEO | video0003 | Runing hour | 239 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Runing hour
239 | 3 |  | COMPRESSOR 01 | COMPRESSOR 01 | STANDBY MODE | IMAGE | compressor_01 | You are about to inspect compressor 01 | 240 | 1 | 0 | com-05 | 1 | 248 |  | NONE | [5 empty] | compressor 01
240 | 3 |  | OIL LEVEL | COMPRESSOR 01 | STANDBY MODE | IMAGE | imag0036 | Oil level | 241 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Oil level
241 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 01 | STANDBY MODE | IMAGE | imag0037 | Check oil leaking | 242 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
242 | 3 |  | CHECK OIL LEAKING | COMPRESSOR 01 | STANDBY MODE | IMAGE | imag0040 | Check oil leaking | 243 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
243 | 3 |  | VALVE OPEN | COMPRESSOR 01 | STANDBY MODE | IMAGE | imag0041 | Valve open | 244 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Valve open
244 | 3 |  | AIR PRESSURE | COMPRESSOR 01 | RUN MODE | VIDEO | video0004 | Air pressure | 245 | 0 | 0 |  | 0 |  |  | DECIMAL |  | BAR |  | 6 | 7.5 | Air pressor
245 | 3 |  | CHECK COOLANT TEMPERATURE | COMPRESSOR 01 | RUN MODE | VIDEO | video0004 | Check coolant temperature | 246 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 70 | 110 | Check coolant tempracher
246 | 3 |  | CHECK DISCHARGE TEMPERATURE | COMPRESSOR 01 | RUN MODE | VIDEO | video0004 | Check discharge temperature | 247 | 0 | 0 |  | 0 |  |  | DECIMAL |  | F |  | 80 | 95 | Check discharge tempracher
247 | 3 |  | RUNING HOUR | COMPRESSOR 01 | RUN MODE | VIDEO | video0004 | Runing hour | 248 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Runing hour
248 | 3 |  | AIR DRYER O1 | AIR DRYER O1 | STANDBY MODE | IMAGE | dryer_01 | You are about to inspect air dryer 1 | 249 | 1 | 0 | com-06 | 1 | 253 |  | NONE | [5 empty] | air dryer
249 | 3 |  | CONTROL SWITCH | AIR DRYER O1 | SWITCH ON DRYER | IMAGE | img_3893 | control switch | 250 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | control switch
250 | 3 |  | CHECK PRESSURE | AIR DRYER O1 | PRESSER GAUGE | IMAGE | img_3893 | Check pressure | 251 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Check pressure
251 | 3 |  | CHECK OIL LEAKING | AIR DRYER O1 | VISUAL CHECK | IMAGE | img_3895 | Check oil leaking | 252 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
252 | 3 |  | CHECK OIL LEAKING | AIR DRYER O1 | VISUAL CHECK | IMAGE | img_3896 | Check oil leaking | 253 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
253 | 3 |  | AIR DRYER O4 | AIR DRYER O4 | STANDBY MODE | IMAGE | dryer_04 | You are about to inspect air dryer 4 | 254 | 1 | 0 | com-07 | 1 | 258 |  | NONE | [5 empty] | air dryer
254 | 3 |  | CONTROL SWITCH | AIR DRYER O4 | SWITCH ON DRYER | IMAGE | imag0050 | control switch | 255 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | control switch
255 | 3 |  | CHECK PRESSURE | AIR DRYER O4 | PRESSER GAUGE | IMAGE | imag0051 | Check pressure | 256 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Check pressure
256 | 3 |  | CHECK OIL LEAKING | AIR DRYER O4 | VISUAL CHECK | IMAGE | imag0052 | Check oil leaking | 257 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
257 | 3 |  | AIR DRYER O3 | AIR DRYER O3 | STANDBY MODE | IMAGE | dryer_03 | You are about to inspect air dryer 3 | 258 | 1 | 0 | com-08 | 1 | 263 |  | NONE | [5 empty] | air dryer
258 | 3 |  | CONTROL SWITCH | AIR DRYER O3 | SWITCH ON DRYER | IMAGE | imag0047 | control switch | 259 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | control switch
259 | 3 |  | CHECK PRESSURE | AIR DRYER O3 | PRESSER GAUGE | IMAGE | imag0048 | Check pressure | 260 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Check pressure
260 | 3 |  | CHECK OIL LEAKING | AIR DRYER O3 | VISUAL CHECK | IMAGE | imag0049 | Check oil leaking | 261 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
261 | 3 |  | AIR DRYER O2 | AIR DRYER O2 | STANDBY MODE | IMAGE | dryer_02 | You are about to inspect air dryer 2 | 262 | 1 | 0 | com-09 | 1 | 265 |  | NONE | [5 empty] | air dryer
262 | 3 |  | CONTROL SWITCH | AIR DRYER O2 | SWITCH ON DRYER | IMAGE | imag0042 | control switch | 263 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | control switch
263 | 3 |  | CHECK PRESSURE | AIR DRYER O2 | PRESSER GAUGE | IMAGE | imag0043 | Check pressure | 264 | 0 | 0 |  | 0 |  |  | DECIMAL | [5 empty] | Check pressure
264 | 3 |  | CHECK OIL LEAKING | AIR DRYER O2 | VISUAL CHECK | IMAGE | imag0045 | Check oil leaking | 265 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Check oil leaking
265 | 3 |  | FINISH | GENERAL CHECKUP | FINISH | NONE |  | Well done. You have finished checking compressor room. |  | 0 | 1 |  | 0 |  |  | NONE | [5 empty] | Finish