## GAUGE_NEW
id | domain_id | number | title | main_group | sub_group | visual_type | visual_link | visual_description | next_step | show_map | last_step | map_from_previous_link | enable_skip | skip_to_step | map_from_beginning_link | value_type | value_hint | unit | default_value | default_from_value | default_to_value | report_description
1 | 1 |  | WELCOME | GENERATOR ROOM | SAFETY ITEMS | NONE |  | Welcome to the Generator Room. Please sure wear all required PPEs (personal protection equipments) | 2 | 0 | 0 |  | 0 |  |  | NONE
2 | 1 |  | EAR PROTECTION | GENERATOR ROOM | SAFETY ITEMS | IMAGE | 36 | Please wear the ear protections. | 3 | 1 | 0 | 01 | 0 |  |  | NONE
3 | 1 |  | HELMET WITH LIGHT | GENERATOR ROOM | SAFETY ITEMS | IMAGE | 37 | Please wear the safety helmet. | 4 | 0 | 0 |  | 0 |  |  | NONE
4 | 1 |  | SWITCH ON LIGHT | GENERATOR ROOM | SAFETY ITEMS | NONE |  | Please switch on lights. | 5 | 0 | 0 |  | 0 |  |  | NONE
5 | 1 |  | OIL LEVEL | GENERATOR ROOM | GENARAL | IMAGE | 2.1 | Ensure the Lube oil level with in the allowable limit (Must be at normal range, see the tag) | 6 | 1 | 0 | 02 | 0 |  |  | BOOLEAN | [5 empty] | Oil Level
6 | 1 |  | OIL LEAKS | GENERATOR ROOM | GENARAL | IMAGE | 3 | Inspect to verify NO any oil leaks on or around the engine body. | 7 | 1 | 0 | 03 | 0 |  |  | BOOLEAN | [5 empty] | Oil Leaks
7 | 1 |  | TRACO FILTER | GENERATOR ROOM | FUEL LEAKS | IMAGE | 4 | Inspect to verify NO any fuel leaks on the Traco filters. | 8 | 1 | 0 | 04 | 0 |  |  | BOOLEAN | [5 empty] | Track Filter fuel leaks
8 | 1 |  | PIPE LINE | GENERATOR ROOM | FUEL LEAKS | IMAGE | 4 | Inspect to verify NO any fuel leaks on the floor diesel path ways. | 9 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Pipeline fuel leaks
9 | 1 |  | DAY TANK DEISEL LEVEL | GENERATOR ROOM | DIESAL TANK | IMAGE | 5 | Check and log day tank Diesal level. | 10 | 1 | 0 | 05 | 0 |  |  | DECIMAL |  | L |  | 1800 | 2300 | Day tank diesal level
10 | 1 |  | MAIN TANK DEISEL LEVEL | GENERATOR ROOM | DIESAL TANK | IMAGE | 34 | Check the availability level of diesel level in Main Storage | 11 | 0 | 0 |  | 0 |  |  | DECIMAL |  | L |  | 7500 | 99999 | Main tank diesal level
11 | 1 |  | BATTERY VOLTAGE | GENERATOR ROOM | CONTROL PANEL | VIDEO | 6 | Check and log the battery voltage. | 12 | 1 | 0 | 06 | 0 |  |  | DECIMAL |  | V |  | 24 | 28 | Control panel Battery Voltage
12 | 1 |  | kWh | GENERATOR ROOM | CONTROL PANEL | VIDEO | 7 | Check and log the total kWh. | 13 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kWh |  |  |  | Control panel kWh
13 | 1 |  | RUNNING HOURS | GENERATOR ROOM | CONTROL PANEL | VIDEO | 8 | Check and log the total running hours. | 14 | 0 | 0 |  | 0 |  |  | DECIMAL |  | h |  |  |  | Control panel Running hours
14 | 1 |  | HEATER COIL | GENERATOR ROOM | ALTERNATOR | IMAGE | 9 | Check the heater coil condition(Touch and feel the warm condition of the alternator housing) | 15 | 1 | 0 | 09 | 0 |  |  | BOOLEAN | [5 empty] | Alternator Heater Oil
15 | 1 |  | AIR RESTRICTION GUAGE | GENERATOR ROOM | AIR FILTER | IMAGE | 10 | Check the indicator of AIR RESTRICTION GAUGE (Indicator color - None is OK) | 16 | 1 | 0 | 10 | 0 |  |  | BOOLEAN |  | Green |  |  |  | Air restriction gauge
16 | 1 |  | BATTERY CHARGER INDICATOR | GENERATOR ROOM | BATTERY CHARGER | IMAGE | 11 | Make sure the battery charger is ON mode(Check the indicator bulb is Lightup) | 17 | 1 | 0 | 11 | 0 |  |  | BOOLEAN | [5 empty] | Battery Charger Indicator
17 | 1 |  | BATTERY WATER LEVEL | GENERATOR ROOM | BATTERY CONDITION | IMAGE | 12.1 | Check the battery water level. | 18 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Battery water level
18 | 1 |  | WIRE TERMINALS | GENERATOR ROOM | BATTERY CONDITION | IMAGE | 31 | Check the battery wire terminal conditions. | 19 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Wire terminals
19 | 1 |  | TENSION | GENERATOR ROOM | RADIATOR FAN | IMAGE | 13 | Check the radiator fan belt tension. | 20 | 1 | 0 | 13 | 0 |  |  | BOOLEAN | [5 empty] | Radiator fan tension
20 | 1 |  | PHYSICAL DAMAGES | GENERATOR ROOM | RADIATOR FAN | IMAGE | 30 | Check the radiator fan belt physical damages. | 21 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Radiator fan damages
21 | 1 |  | COOLENT LEVEL | GENERATOR ROOM | RADIATOR COOLENT | IMAGE | 14 | Check the radiator coolant at the required level through the side glass. | 22 | 1 | 0 | 14 | 0 |  |  | BOOLEAN | [5 empty] | Radiator Coolent Level
22 | 1 |  | SELECTOR SWITCH | GENERATOR ROOM | SELECTOR SWITCH | VIDEO | 15 | Switch on the Generator manually (select the rotator switch to "Manual" mode and press "Manual Run/Stop" button. | 23 | 1 | 0 | 15 | 0 |  |  | NONE
23 | 1 |  | LINE VOLTAGE | GENERATOR ROOM | CONTROL PANEL | VIDEO | 16 | Check and log the line voltage. | 24 | 0 | 0 |  | 0 |  |  | DECIMAL |  | V |  | 395 | 411 | Control panel Line voltage
24 | 1 |  | FREQUENCY | GENERATOR ROOM | CONTROL PANEL | VIDEO | 17 | Check and log the frequency. | 25 | 0 | 0 |  | 0 |  |  | DECIMAL |  | Hz |  | 49.5 | 50.5 | Control panel Frequency
25 | 1 |  | AMPHERE | GENERATOR ROOM | CONTROL PANEL | VIDEO | 18 | Check the Amphere. (Only the Generator in running with the load) | 26 | 0 | 0 |  | 1 | 26 |  | DECIMAL |  | A |  |  |  | Control panel Amphere
26 | 1 |  | OIL PRESSURE | GENERATOR ROOM | CONTROL PANEL | VIDEO | 19 | Check and log the oil pressure. | 27 | 0 | 0 |  | 0 |  |  | DECIMAL |  | kPa |  | 520 | 532 | Control panel Oil Pressure
27 | 1 |  | RPM | GENERATOR ROOM | CONTROL PANEL | VIDEO | 20 | Check and log the RPM | 28 | 0 | 0 |  | 0 |  |  | DECIMAL |  | rpm | 1500 |  |  | Control panel RPM
28 | 1 |  | SYSTEM ABNORMALITIES | GENERATOR ROOM | EXHAUST SYSTEM | IMAGE | 21 | Check the exhaust system abnormalities (Color, Sound, Vibration, and etc.) | 29 | 1 | 0 | 21 | 0 |  |  | BOOLEAN | [5 empty] | System Abnormalities
29 | 1 |  | OIL HORSES | GENERATOR ROOM | OIL LEAKS | IMAGE | 33 | Inspect to verify NO oil leaks in oil horses | 30 | 1 | 0 | 22 | 0 |  |  | BOOLEAN | [5 empty] | Oil Horses oil leaks
30 | 1 |  | ENGINE | GENERATOR ROOM | OIL LEAKS | IMAGE | 22 | Inspect to verify NO oil leaks in engine | 31 | 0 | 0 |  | 0 |  |  | BOOLEAN | [5 empty] | Engine oil leaks
31 | 1 |  | FILTERS | GENERATOR ROOM | OIL LEAKS | IMAGE | 32 | Inspect to verify NO oil leaks in filters | 1 | 0 | 1 |  | 0 |  |  | BOOLEAN | [5 empty] | Filter oil leaks